## Slide 1
Asian Development Institute for Community Economy and Technology
Hathaithip Sintuya
Community DC-AC Microgrid
Training on Renewable Energy Policy Tools and Energy Technologies Best Practice
adiCET, Chiang Mai, Thailand
November 22, 2018
APEC Training Workshop on Solar Technology Application

## Slide 2
Smart Cities Driven by Energy 4.0
Digital Society
(Digital Disruption)
Low Carbon
(Decarbonized)
User Changes Producer
(Prosumer)




## Slide 4
Thailand Smart Cities
Thailand Smart Cities

## Slide 5
adiCET, CMRU

## Slide 6: adiCET, Chiang Mai Rajabhat University (CMRU)
Academic – R&D – Training institution for the well-being of the community by using green technologies.
  Graduate Program in Community Economy and Technology
  Model Community with green technologies and renewable energy
  Hybrid System – Smart Community Microgrid

## Slide 7
Renewable Energy & Green Technology Integration for
Local Community Development

## Slide 8
Goal
SPP Hybrid Demo Site
Smart Community Training Center
Green Technology Living Laboratory
Notes: This is how the power is distributed to the houses

## Slide 9
Chiang Mai World Green City: Real Living Learning Park
Bioenergy
Energy Efficiency
10 New Smart Homes
Grid Connected
Energy Storage
DC & AC Microgrid
Green Business
Smart Farm
Notes: Now I would like to explain about the Zone A which is the smart community –The smart community uses 100% renewable energy and strive to be sustainable community. Students & staff of adiCET lived here. We also opened many houses to the general public to experience the sustainable way of living.

## Slide 10: Community DC-AC Microgrid adiCET, CMRU

## Slide 11
Community DC-AC power system
Chiang Mai World Green City (CWGC) model

## Slide 12: PV Systems ~ 762 kWp
702 kW
Grid Connected
25.5 kW DC Microgrid
Off Grid
25 kW AC Microgrid
Grid Connected
3.5 kW Rooftop
2.64 kW Stand Alone
EV Charging Station
3 kW
Water
Pumping

## Slide 13: 702 kW - Grid Connected

## Slide 14: 25 kW DC Off-Grid & 25 kW AC Grid Connected

## Slide 15: 3.5 kW Rooftop Grid Connected

## Slide 16
Chiang Mai World Green City: Real Living Learning Park
Community
Product
Green Resort
Community
Restaurant
Natural Material Building
Exhibition Center
Recycle Road
Energy Efficient Building
Community
Business
Energy
Crop
Wood chip
Wood pellet
Hydroponics
Fertilizer Organic wastes
Low Carbon
Agriculture
Smart Water System
Biodiesel Generator
DC Home
PV Grid Connected
AC Microgrid
Solar Pumping
DC Microgrid
Community Solar Farms
PV Stand Alone
Biogas
Biomass
Gasifier
Household
Biogas
Community Power Training Center
Notes: องค์ประกอบของ Chiang Mai World Green City เกิดมาจาก งานวิจัยและบริการวิชาการกว่า 50 โครงการ

## Slide 17: Scope of DC Community
Living Laboratory for community transition from AC  AC/DC  DC Community
Evaluate Low Cost - Low Voltage DC Community Power System at the Smart Community
  Phase 1: Lightings 24 VDC/ 1 House 240 VDC
  Phase 2: Household Appliances 260-297 VDC
Modify/Testing Household Appliances for DC & AC usage
  Lighting, Refrigerator, Air Conditioner, Water Heater, Television, Computer, Rice Cooker, Microwave, Washing Machine
Evaluate appliances during operation, stability and safety
  Full DC
  Full AC
  Mixed DC & AC
Notes: ขอบเขตของงานวิจัยนี้ คือ
ทดสอบภาระทางไฟฟ้าด้วยโครงข่ายไฟฟ้ากระแสตรงแรงดันต่ำ ที่วิทยาลัยพัฒนาเศรษฐกิจและเทคโนโลยีชุมชน
2. ดัดแปลงปรับปรุงภาระทางไฟฟ้าต่าง ๆ ให้สามารถใช้ไฟฟ้ากระแสตรงได้ โดยภาระทางไฟฟ้าที่ระบบเซลล์แสงอาทิตย์ที่พัฒนาขึ้นประกอบด้วย หลอดไฟ ตู้เย็น เครื่องปรับอากาศ เครื่องทำน้ำร้อน และโทรทัศน์
3. ทดสอบสมรรถนะทางด้านเทคนิค ความเสถียรภาพ และความปลอดภัยของภาระทางไฟฟ้า

## Slide 18: PV AC vs. PV DC
PV Array
Charge Controller
Battery
DC Load
DC
DC
PV Array
Charge Controller
Battery
AC Load
Inverter
DC
DC
AC
DC Load
DC
DC
Higher system efficiency by eliminating DC/AC/DC conversion
Lower cost from eliminating inverter

## Slide 19
DC,
323 V
80 A (Max)
PV Array
25.5 kWp
Charge Controller
Battery
105.6kWp
DC, 264-297 V
DC Load
DC, 323 V 80 A (Max)
System Design and Installation
Converter
to 24 VDC
DC Load
Lighting
DC
24 V
600 W
1st Phase
2nd Phase
Notes: ภาพนี้แสดงการออกแบบระบบโรงไฟฟ้าที่ติดตั้ง เพื่อทำการทดสอบการไฟฟ้ากระแสตรง 264V
ซึ่งออกแบบระบบโซล่าเซลล์ให้มีขนาด 25.5 kW เป็นแหล่งผลิตไฟฟ้า
ชาร์เจอร์เป็นอุปกรณ์ช่วยควบคุมการประจุแบตเตอรี่ส่งถ่ายไฟฟ้าไปยังโหลด

## Slide 20
25.5 kW
Battery: 105.6 kW
DC Microgrid
Load:
1 office, 1 minimart,
1 restaurant,
1 coffee shop,
1 farm, 4 houses
Utility & 25 kW
AC Microgrid
Diesel Generator 40kW
Notes: The power cables are underground to each of the building

## Slide 21: Smart Community – AC/DC Smart Grid
Load:
1 office
1 minimart,
1 restaurant
1 coffee shop
1 farm
6 houses
Biogas
DC PV System
Biomass Gasifier
Biodiesel
Generator
Office
Home
Home
Home
Home
Coffee Shop
Restaurant
Smart Farm
Minimart
AC PV System
Home
Home

## Slide 22
PV DC Microgrid
25.5 kW
PV AC Microgrid
25 kW
Biodiesel Generator
40 kW
Biomass Gasifier
20 kW

## Slide 23
Battery House
On-grid: PV AC Microgrid Battery Bank (~100 kWh)
Backup power/ Power Control and Stability
Off-grid: PV DC Microgrid Battery Bank (~100 kWh)
Backup power/ Power Control and Stability

## Slide 24
Convert All Electrical Devices to DC Usage
Install Power Supply Controller
Install Booster Battery

## Slide 25
Notes: Each building has a converter box for the DC conversion.

## Slide 26
Home energy monitoring system
DC & AC Smart plug

## Slide 27
Expanded Polystyrene Foam
Home monitoring system: Temp, Humidity, Wind Speed
Notes: This house is from EPS foam. All the interior is made out of foam as well.

## Slide 28
Home monitoring system: Temp, Humidity, Wind Speed

## Slide 29
Reuse material house

## Slide 30
Resident
Insulation
Construction material for hot & humid climate

## Slide 31
Office

## Slide 32: Power Supply Controller
DC
Battery
Central Battery Bank – DC
AC – Utility
AC Microgrid
Load
DC – AC
Switch
Alarm

## Slide 33: Operation Mode
Mode | Central Battery Voltage Stage | Usage
Full | 297 – 260 VDC | DC use directly from Central Battery bank
Battery Boosting | 260 – 250 VDC | DC from Battery bank (260 VDC) & Booster (54 VDC)
Biodiesel Generator Start | 250 – 242 VDC | Generator Charge Battery Bank Charge Booster Batteries If ran out of fuel, AC from Utility will convert to DC
Battery dead | Below 242 VDC | Automatically switch to AC
Note: Voltage range depends on Charger Specification, battery voltage range and electrical load device requirements.

## Slide 34: Experimental Setup Hybrid DC Microgrid
297 – 260 VDC – CB
260 – 250 VDC – CB + BB
250 – 242 VDC – Gen

## Slide 35
Data Monitoring

## Slide 36: Normal Operation + Battery Boost

## Slide 37: Diesel Generator Mode

## Slide 38: DC and AC Selection

## Slide 39: Building Power Consumption
Building Energy Consumption (W)

## Slide 40: adiCET DC Smart Plug
Online Function
Safety
Smart Function
Controls
Monitors
Program
Web and Application
Power consumption
Behavior
Smart Connection
Smart Data Collection
Energy saving
Prototype for DC Smart Plug
Measurement Function
N. Songkittirote – M.S.
Notes: Now, we are developing the DC Smart Plug to control the appliances in the house

## Slide 41: adiCET DC SmartHome

## Slide 42: adiCET DC Smart Plug Prototype

## Slide 43
Solar Bus Stop
EV
Solar Bus Stop
EV Charging Station
T. Jaorum - Intern
W. Luangpraditkul - Researcher
Motorbike Charging Station
Energy Storage
Notes: We have road. We also have electric vehicle. Our student develop the charging system and make the bus stop with Solar Cells and battery stored down at the benches.

## Slide 44
EPS Foam Energy Efficient House
Home/Building Cycle  Energy efficient – Natural Material
Notes: This house is from EPS foam. All the interior is made out of foam as well.

## Slide 45
Energy Efficient Conference Room
Expanded Polystyrene (EPS) FOAM

## Slide 46
Residence
Notes: Different style of housing from traditional house to low cost housing to expensive energy efficient housing.

## Slide 47
Natural Material Conference Room
Notes: The design of the Turtle back conference hall emphasize on the the use of natural material. The usage of leaves as the roof is conventional in the rural area and we apply it in a modern style. The location of the conference hall has good wind flow which create a comfortable atmosphere all day long.

## Slide 48
Reuse material house

## Slide 49
Office

## Slide 50
Waste Plastic Road

## Slide 51
Chiang Mai World Green City Carbon Emissions
CO2 Sequestrations
CO2 Emissions
Chiang Mai World Green City
Goal – Low Carbon Society
X2 Renewable Energy
X1 Green Area
X3 Green Building
X5 Reduce Reuse Recycle
X4 Energy saving from Lighting
X6 Smart Transportation
X8 Waste, Water, Fuel
X7 Electricity Consumption
X9 Transportation
X0 Emission from Construction
Driving Variables (N) Population | Constant Variable (X0) Emission from the beginning of construction | Sequestration Group (X1-X6) | Emission Group (X7-X9)
adiCET staff with permanent resident adiCET staff with non-permanent resident Student Visitors | X01 Loss of tree from developed land X02 Cut and fill jobs from land development X03 Carbon footprint building 16 units X04 Emission of asphalt road | X1 CO2 intake from green area X2 Electricity production from PV and Gasifier X3 Energy saving from green design building X4 Energy saving from lighting system X5 Environment management X5W 3R3 project of plastic and organic waste X5H 3R3 project of water X5C Bio-Char project X6 Smart transportation | X7 Electricity Consumption X8 Emission from waste, water used and fuel X9 Emission from Transportation
Variables kgCO2e
X01 62,065
X02 51,888
X03 63,199
X04 54,795
Total 231,947
The CO2 cycle assessment of CWGC model was employed to establish a green city master plan and operational plan for low carbon society at adiCET. adiCET aims to be the first practical carbon neutral community in Thailand.

## Slide 52: Business as Usual/ Ideal Condition
Chart: The net accumulated CO2 In 15 Years
 | 188487.6118 | 130414.8242 | 68241.4821 | 23948.1851 | 766.8513 | -8752.9733 | -14180.3598 | -13379.1143 | -18612.788 | -17631.0308 | -15966.6402 | -14302.2496 | -12637.859 | -10973.4684 | -9309.0777
The net accumulated Carbon : 2,001,834 KgCO2
Carbon Credit : -979,897 THB
(Ref : 489.5 THB/T/CO2: 2554)
Ideal condition
No activity of CO2 Mitigation (BAU)
No use of Renewable Energy
No change in energy efficient device
No recycling and waste management
Inefficient transportation
Excess energy usage
Green Activity
Green Space, Tree planting
Renewable Energy usage
Efficient Lighting/ No. 5 Devices
Waste management and biomass usage
Water management
Energy efficient transportation and biofuel

## Slide 53: Issues to Overcome
System Issues
  During the rain, the voltage fluctuates from the utility line which cause the Hybrid Microgrid system to be disrupted.
  The old power meter in the smart community causes damage to the power monitoring unit during the voltage fluctuations.
  The university change the IP address and this causes failed data recorder. The online connectivity is still a problem.
  When using AC as backup power, there are some back flow of current.
  The capacitor was damaged when AC was used over the voltage setting.
  Explore voltage range for Diesel Generator
Nature Issues
Human Issues

## Slide 56: Conclusion
The direct current PV system is able to supply sufficient power to each house in the Smart Community
There were a lot of system on-site trouble shooting do to nature and behavior of user
Notes: The low voltage direct current system was used to supply direct-DC power to modified household appliances include LED lighting, refrigerator, air conditioner, television and electric water heater. The results indicated that the power consumption from the modified appliances is lower when DC power was used in comparison to AC power. The highest energy savings was LED lighting with 38%. However, with high power rating appliances, there are no significant difference for the energy savings between DC and AC usage. The power consumption profiles for the appliances are quite stable indicating the DC power quality. As a result, for the rural community application, the household appliances can be modified with simple and affordable techniques to comply with DC power. The modified appliances can be used efficiently with solar home systems or community decentralized PV systems with direct-DC distribution.

## Slide 57: Acknowledgments
NICOP Grant from the Office of Naval Research, USA
Ministry of Energy, Thailand
National Research Council of Thailand
Chiang Mai Rajabhat University
Uttaradit Rajabhat University
ASEAN – U.S. Science and Technology Fellowship

## Slide 58
Contacts:
Website: www.adicet.cmru.ac.th Email: hathaithip.nin@gmail.com
Facebook: www.facebook.com/adicetfan Phone: +6653-885871
Thank You